Electrical Equipment Troubleshooting Guide

Comprehensive diagnostic chart for contacts, coils, overload relays, controllers, and mechanical parts.

| Part / Category | Problem | Cause | Remedy |
| --- | --- | --- | --- |
| Contacts | Contact Chatter (also see Noisy Magnet) | 1. Poor contact in the control circuit. 2. Low voltage. | 1. Replace the contact device or use a holding circuit interlock (three-wire control). 2. Check the coil terminal voltage and voltage dips during starting. |
| Contacts | Welding or Freezing | 1. Abnormal inrush of current. 2. Rapid jogging. 3. Insufficient tip pressure. 4. Low voltage which prevents the magnet from sealing. 5. Foreign matter prevents the contacts from closing. 6. Short circuit or ground fault. | 1. Check for grounds, shorts, or excessive motor load current, or use larger contactor. 2. Install a larger device rated for jogging service. 3. Replace contacts and springs. Check contact carrier for deformation or damage. 4. Check the coil terminal voltage and voltage dips during starting. 5. Clean the contacts with an environmentally safe (CFC-free) contact cleaner. 6. Remove the cause of the event. Make sure that the fuse and circuit breaker sizes are correct. |
| Contacts | Short Trip Life or Overheating or Trips | 1. Filing or dressing. 2. Interrupting excessively high currents. 3. Excessive jogging. 4. Weak tip pressure. 5. Dirt or foreign matter on the contact surface. 6. Short circuit or ground fault. 7. Loose connection in the power circuit. 8. Sustained overload. | 1. Do not file the silver tips; rough spots or discoloration do not harm tips or impair their efficiency. 2. Install a larger device or check for grounds, shorts, or excessive motor currents. 3. Install a larger device rated for jogging service. 4. Replace contacts and springs; check the contact carrier for deformation or damage. 5. Clean contacts with a CFC-free contact cleaner. Reduce entry of foreign matter into enclosure. 6. Remove cause of event; ensure fuse and circuit breaker sizes are correct. 7. Clear and tighten connection. 8. Check for excessive motor load current or install larger device. |
| Coils | Open Circuit | Mechanical damage. | Replace the coil; handle and store replacement coils carefully. |
| Coils | Overheated Coil | 1. Overvoltage or high ambient temperature. 2. Incorrect coil. 3. Shorted turns caused by mechanical damage or corrosion. 4. Undervoltage; magnet will not seal in. 5. Dirt or rust on the pole faces. 6. Mechanical obstruction. | 1. Check coil terminal voltage. It should not exceed 110% of coil rating. 2. Install correct coil. 3. Replace coil. 4. Check coil terminal voltage. It should be at least 85% of coil rating. 5. Clean pole faces. 6. With power off, check for free movement of contact and armature assembly. |
| Thermal Overload Relays | Tripping | 1. Sustained overload. 2. Loose or corroded connection in power circuit. 3. Incorrect thermal units. 4. Excessive coil voltage. | 1. Check for excessive motor currents or current unbalance; correct cause. 2. Clean and tighten connection. 3. Replace thermal units with correct size for application. 4. Voltage should not exceed 110% of coil rating. |
| Thermal Overload Relays | Not Tripping | 1. Incorrect thermal units. 2. Mechanical binding, dirt, or corrosion. 3. Relay previously damaged by short circuit. 4. Relay contact welded or not in series with contactor coil. | 1. Check thermal unit selection table. Install proper thermal units. 2. Replace relay and thermal units. 3. Replace relay and thermal units. 4. Check circuit for cause of event and correct condition. Replace contact or entire relay as necessary. |
| MotorLogic Overload Relays | Overload relay trips on start-up (after > 3s) | 1. Load too heavy for motor horsepower. 2. Wrong overload trip class selected. 3. Incorrect overload FLA setting. 4. Use of electronic DC injection brake. | 1. Remove excessive motor load or resize motor. 2. Use Trip Class 20 overload relay instead of Trip Class 10. 3. Set FLA adjustment according to motor full-load current. 4. Do not use electronic DC injection brakes with solid-state overload relay. |
| MotorLogic Overload Relays | Overload relay trips on start-up (in < 3s) | 1. Motor branch circuit fuse blown. 2. Loose motor branch circuit. 3. Motor circuit is not three-phase. 4. Voltage unbalance on feeder. 5. Motor winding damage. 6. Phase loss in transformer primary. 7. Load lead(s) not routed correctly through relay window. 8. Pass counts are different. | 1. Replace blown motor branch circuit fuse(s). 2. Tighten motor branch circuit connection. 3. Select different overload relay for non three-phase applications. 4. Correct voltage unbalance on feeder. 5. Check motor winding impedance. Rewind if necessary. 6. Replace blown fuses or tighten connections. 7. Pass each load lead through window in same direction. 8. Each load lead must be looped same number of passes. |
| MotorLogic Overload Relays | Overload relay trips while running normally | 1. Load too heavy for motor horsepower. 2. Incorrect overload FLA setting. 3. Use of electronic DC injection brake. 4. Incorrect overload FLA setting (multiple passes). | 1. Remove excessive motor load or resize motor. 2. Set FLA adjustment according to motor full-load current. 3. Do not use electronic DC injection brakes with solid-state overload relay. 4. Recalculate FLA adjustment based on full-load current and looped passes. |
| TeSys T Motor Controller | Minor internal detected errors | Invalid configuration (bad checksum or bad data from hardware misoperation). | 1. Cycle power and wait 30 s. 2. Reset configuration settings to factory settings. 3. If condition persists, replace TeSys T motor controller. |
| TeSys T Motor Controller | Configuration checksum / Loss of internal comms / A/D out of range | Hardware misoperation. | 1. Cycle power and wait 30 s. 2. If condition persists, replace TeSys T motor controller. |
| TeSys T Motor Controller | Diagnostic (Start/Stop command checks, Run check back) | Control/Power/Load CT wiring or output failure. | Check relay outputs and all wiring (control, power, load CT). 1. Perform a reset. 2. If condition persists, cycle power and wait 30 s. 3. Replace TeSys T motor controller. |
| TeSys T Motor Controller | Wiring/configuration errors | CT reversal / Phase reversal / PTC connection / Phase loss | Correct CT polarity, verify L1/L2/L3 sequence, check temp sensor wiring, verify line voltage and fuses. 1. Perform a reset. 2. Cycle power and wait 30 s. 3. Replace controller if condition persists. |
| TeSys Tera Overload Relays | Diagnostics & Wiring Errors | Start/Stop check faults, CT Reversal, Phase Reversal, PTC Connection, Phase Loss | Perform full wiring/phase/sensor check. 1. Perform a reset. 2. Cycle power and wait 30 s. 3. Replace TeSys Tera motor controller if condition persists. |
| TeSys Tera Overload Relays | Major Internal Malfunctions | Sensor module comm error, expansion module comm error, configuration error, or high internal temp. | 1. Check RJ11/RJ45 connections. 2. Verify DTM 'my device' configuration and CT/VT settings. 3. Replace cables, expansion/sensor module, or main LTMT unit as required. |
| TeSys Tera Overload Relays | Minor Internal Malfunctions | Internal error detected. | Contact Schneider support team. |
| Magnetic & Mechanical Parts | Noisy Magnet | 1. Broken shading coil. 2. Dirt or rust on magnet faces. 3. Low voltage. | 1. Replace magnet and armature. 2. Clean magnet with clean, dry cloth. 3. Check coil terminal voltage and voltage dips during starting. |
| Magnetic & Mechanical Parts | Does Not Pick Up and Seal | 1. No control voltage. 2. Low voltage. 3. Mechanical obstruction. 4. Open or overheated coil. 5. Wrong coil. | 1. Check control circuit wiring for loose connection/continuity. 2. Check coil terminal voltage and starting dips. 3. With power off, check free movement of contact/armature. 4. Replace coil. |
| Magnetic & Mechanical Parts | Does Not Drop Out | 1. Gummy substance on pole faces. 2. Voltage not removed. 3. Worn/corroded binding parts. 4. Residual magnetism. 5. Welded contacts. | 1. Clean pole faces with clean, dry cloth. 2. Check coil terminal voltage and control circuit. 3. Replace worn parts / magnet assembly. 4. Refer to Contacts—Welding or Freezing. |
| Pneumatic Timers | Erratic Timing / Contacts Do Not Operate | Foreign matter in valve, actuating screw maladjustment, or worn snap switch. | Replace timing head/snap switch or return timer for repair. Adjust per service bulletin. |
| Limit Switches | Broken Parts | Over-travel of actuator. | Use resilient actuator or operate within device tolerance. |
| Manual Starters | Does Not Reset | Latching mechanism worn or broken. | Replace starter. |